Typical Specifications

TYPE PNI SF6 INSULATED PAD MOUNT SWITCHGEAR

FRONT ACCESS STYLE

PART 1- GENERAL

1.1	DESCRIPTION

- The switch shall consist of manually operated load interrupting, SF6 insulated, 630A linear puffer switches and manually operated, electronically controlled fault interrupters.  The switches shall be designated G&W PNI style.

1.2	QUALITY ASSURANCE

A.	Manufacturer Qualifications:  The chosen manufacturer shall have at least 30 years experience in manufacturing SF6 insulated medium voltage switchgear.  The manufacturer of the switches shall be completely and solely responsible for the performance of the load break switch and fault interrupter as well as the complete integrated assembly as rated.

B.	The manufacturer shall furnish certification of ratings of the load break switch, fault interrupter and the integrated switch assembly upon request.

C.	The switch shall comply with requirements of the latest revisions of applicable industry standards, including:

IEEE C57.12.28, IEEE C37.72, IEEE C37.74, IEEE C37.60, IEEE 386

D.	The switch manufacturer shall be ISO 9001 and 14001 certified.

1.3	DELIVERY, STORAGE, AND HANDLING

A.	Load break switches and fault interrupters shall be shipped preassembled at the factory.  No field assembly shall be required.

B.	The contractor, if applicable, shall handle, transfer and move the switches in accordance with manufacturer’s recommendations.

PART 2- PRODUCTS

2.1	SWITCH CONFIGURATION

A.	Each switch shall be equipped with 3-phase load break switch ways and 3-phase fault interrupter ways, as indicated on the one-line diagram.

B.	Switches shall be designed for front access to cables and operators.

2.2	SWITCH CONSTRUCTION

A.	General

Switch contacts and cable entrance terminations shall be contained in a single welded mild steel tank with entrances internally connected by copper conductors.  Construction shall be a dead front design.  Switches shall be shipped factory filled with SF6 gas conforming to ASTM D-2472.  Switch tanks shall be painted ASA70 light gray using a corrosion-resistant epoxy paint.

- Load Break Switch

Each switching way is to be equipped with an internally mounted operating mechanism capable of providing quick-make, quick-break operation in either switching direction. The mechanism must be capable of delivering sufficient torque and shall be provided with latches for each position to assure load interrupting, fault closing and momentary ratings. All switch positions are to be clearly identified, padlockable and adaptable to keylock schemes. The operating mechanism shall be actuated from outside the switch tank with an operating handle. The operating shaft shall be made of stainless steel for maximum corrosion resistance. A double “O” ring type operating shaft seal shall be used for a leak resistant, long life seal. Switch contacts shall be a tulip-bayonet design and made of plated, high-conductivity copper alloy with arcing tips of copper/tungsten alloy to assure permanent low resistance and to avoid sticking during operations. The contacts shall be designed such that arcing does not occur in the area of main current interchange and contact pressure will increase with increased current flow. The stationary contacts shall be supported independent of the cable entrance bushings, eliminating possible misalignment. The contact nozzle shall have a converging/diverging geometry which improves the flow of SF6 into the arc zone. Contact travel shall be a minimum of 3 inches and have sufficient open contact separation to assure efficient arc extinction and to withstand field DC testing levels and maintain BIL levels. Switch contacts shall be clearly visible in the open position through viewing windows. Auxiliary blades used for load interruption are not acceptable.

C.	Fault Interrupters

The fault interrupter shall consist of vacuum bottles and a spring-assisted operating mechanism.  The mechanism used shall be designated "Model NI" for three phase operation.  The mechanism shall consist of three vacuum bottles mechanically linked to a single spring-assisted operating mechanism.  The fault interrupter operating mechanism shall consist of the support assembly, linkage, spring latch mechanism, and solenoid utilized for electronic tripping.  Maximum interrupting time shall be three cycles (50 msec).  The movable contact shaft shall be flagged to indicate the contact position, open or closed.  This contact position indicator shall be fully visible through viewing windows supplied in the switch tank.  Each tap phase is to be equipped with an individual 630A vacuum interrupter fully enclosed in an SF6 insulated switch tank.  Electrical opening shall be by a solenoid that is activated from sources external to the switch tank.  Manual reset or closing of the fault interrupter shall be mechanical with the use of an external operating handle.  The mechanical linkage assembly shall provide for a "trip-free" operation which allows the fault interrupter to interrupt independent of the operating handle.

2.3	DESIGN RATINGS

A.	Switch Ratings - the switch shall be rated (choose appropriate column):

| SELECTION OF RATINGS | IEEE/IEC |  |  |
| --- | --- | --- | --- |
| Maximum Design Voltage, kV | 15.5 | 27 | 38 |
| Impulse Level (BIL) Voltage, kV | 110 | 125 | 150 |
| Continuous Current, Amperes | 630 | 630 | 630 |
| Load break Current, Amperes | 630 | 630 | 630 |
| One Minute Withstand (dry), AC kV | 35 | 60 | 70 |
| Production Test Rating | 34 | 40 | 50 |
| 15 Minute Withstand, DC kV | 53 | 78 | 103 |
| Momentary Current, kA, ASYM | 40 | 40 | 40 |
| Fault-Close Current, kA, ASYM | 40 | 40 | 40 |
| One Second Current, kA, SYM | 25 | 25 | 25 |
| Fault Interrupting Rating, kA, SYM | 12.5* | 12.5* | 12.5* |
| Mechanical Endurance, Operations | 2000 | 2000 | 2000 |

*Note – 25kA sym fault interrupting rating is available (specifier to change the rating above)

B.  Interrupters shall be tested IEEE C37.60 Fault Interrupting Duty per the table below

| Percent of Maximum: Interrupting Rating | Approx. Interrupting: Current Amps | No. of Fault: Interruptions |
| --- | --- | --- |
| 15-20% | 2000 | 44 |
| 45-55% | 6000 | 56 |
| 90-100% | 12000 | 16 |
| Total Number of Fault Interruptions: 116 |  |  |

2.4	CABLE ENTRANCES

A.	Load Break Switches

Cable entrances shall be tested to IEEE 386 and be, as indicated on the switch drawing:

- ____ 600 amp G&W Quik-Change disconnectable apparatus bushing,

- ____ 200 amp Deepwell bushing.

B.	Fault Interrupters

Cable entrances shall be tested to IEEE 386 and be, as indicated on the switch drawing:

- ____ 600 amp G&W Quik-Change disconnectable apparatus bushing,

- ____ 200 amp Deepwell bushing.

2.5	ELECTRONIC CONTROL

An electronic control shall be provided to monitor load and fault current on all three phases of the fault interrupter.  Each phase shall have a current transformer mounted inside the switch tank to provide control power and current sensing. No external power source shall be required for overcurrent protection. Operational temperature range of the control shall be -40°C to +65°C.  Maximum time for power up and ready-to-trip when closing on a circuit shall be ten percent of the trip time or 1/2 cycle, whichever is greater. Trip selection may be made with the fault interrupter energized.  The range of Phase Overcurrent minimum trip settings shall be 15-300A (500:1 CT) or 30-600A (1000:1 CT) (the specifier must choose)

The specifier must select one of the following controls and options:

Type 2

The control shall include 30 Time Current Characteristic (TCC) curves, which shall be field selectable using dip switches.  The control shall be equipped with multiple TCC curve modification options, including Instantaneous Trip, Inrush Restraint, and Phase Time Delay.  In addition, the control shall include a Phase Imbalance (Ground Fault) setting.   All settings shall be inputted via selector knobs located on the faceplate of the control.   The control shall include a last cause of trip indicator. Trip modules shall not require a computer or other external device for inputting trip settings or other operational parameters.

Type 3 EZSet

The control shall include 30 Time Current Characteristic (TCC) curves.  All settings shall be inputted via the control’s Vacuum Fluorescent Display or via a computer.  The control shall allow for multiple TCC curve modification options, including Instantaneous Trip, Inrush Restraint, and Phase Time Delay.  In addition, the control shall include a Phase Imbalance (Ground Fault) setting.   The control shall allow for the selection of independent TCC curves for Phase Overcurrent and Phase Imbalance (Ground Fault) protection.  The control shall include a Sequence of Events Recorder (SER) which shall record the last 16 causes of trip.  The control programming software shall include password protection, the ability to download the SER, and the ability to save and print setting files.

Type 3 Plus

The control shall include 60 pre-loaded and 5 user created time current characteristic (TCC).  All setting options shall be accomplished using the Vacuum Fluorescent Display or a computer.    In addition, the control shall include a Phase Imbalance (Ground Fault) setting.  The control shall allow for multiple curve modification options for each minimum trip setting (phase and ground) including Instantaneous Trip, Inrush Restraint, and Phase Time Delay.   The control shall allow for two settings groups (protection and alternate).  The control shall allow for two TCC curves for each protection settings group (one for phase and the other for phase imbalance (ground fault)). The control shall include an option for single or three phase trip (Phase Imbalance/ Ground Fault shall not be available when the control is set for single phase trip).  The control shall include a Sequence of Events Recorder (SER) which shall include the last 16 causes of trip. The control programming software shall include password protection, the ability to download the SER, and the ability to save and print setting files.

Options for Electronic Controls

(Specifier to choose as required for the application)

- The control cable shall be connectorized, allowing the electronic control to be removed from the interrupter for repair or replacement while the interrupter is energized.  The interrupter shall include protection circuitry to allow this while preventing any damage to the current transformers.

- The control shall be powered via a (specifier to select one: 24VDC, 48VDC, 120VAC, 220VAC) source.  The control shall include an option to accept a dry contact input that will cause it to initiate a trip signal to the interrupter.

- For Dry Applications:  Control mounted in a NEMA4X rated fiberglass enclosure

- For Wet/ Damp Applications:  Control mounted in a NEMA6P rated fiberglass enclosure

2.6	PAD MOUNT ENCLOSURE

The enclosure shall be fabricated of 12 gauge galvanized steel and manufactured to ANSI C37.72 and C57.12.28 standards.  The enclosure shall be tamper resistant incorporating hinged access doors with pentahead locking bolts and provisions for padlocking. The enclosure shall be provided with lifting provisions and painted with a Munsell 7.0GY3.29/1.5 green finish.

2.7	FACTORY PRODUCTION TESTS

Each switch shall undergo the following production testing.  Test reports must be available upon request

- Each switch shall be factory filled with SF6 gas.  The gas shall be checked for moisture content

- Each switch shall undergo an SF6 leak check to verify the integrity of the tank, seals, and gaskets

- A mechanical operation check of each switching mechanism

- AC hi-pot tested one minute phase-to-phase, phase-to-ground and across the open contacts

- Circuit resistance shall be checked.

- Primary current injection test to test CTs, trip mechanism, and electronic control

2.8	STANDARD COMPONENTS

The following shall be included as standard:

- Mild steel tank

- Fixed operating handles for the load break switches and one (1) removable handle to operate the fault interrupters.

- Gas pressure gauge and fill valve.

- ½-13 nuts to provide sufficient grounding provisions for all cable entrances

- Stainless steel three line diagram and corrosion-resistant nameplates.

- Switch operating handles with padlock provision.

- Parking stands for each bushing

- (1) viewing window per load break switch to view open contact position

- (1) viewing window per fault interrupter to view vacuum bottle position

- Provision to mount future low pressure alarm

2.9 OPTIONS

The following options shall be supplied: (check as appropriate):

- ¼”  304/304L dual certified stainless steel tank

- 12-gauge stainless steel enclosure manufactured to ANSI C37.72 and C57.12.29 standards.  The enclosure shall be tamper resistant incorporating hinged access doors with penta head locking bolts and provisions for padlocking. The enclosure shall be provided with lifting provisions and painted with a Munsell 7.0GY3.29/1.5 green finish.

- Temperature compensating pressure gauge

- Quick disconnect fitting to remove the pressure gauge without loss of SF6 gas

- Low pressure warning device to provide a dry contact if SF6 pressure within the tank falls below 5psig (applicable where ambient temperatures stay above 32°F)

- SF6 density switch to provide a dry contact if SF6 density falls too low (applicable where ambient temperatures may fall below 32°F)

- 4/0 brass ground lug

- Provisions to mount a key interlock after installation

- Keylock installed at the factory, to lock in open position

- Auxiliary switches to mount two (2) Form C contacts for remote switch position indication of the load break switch

- Auxiliary switches to mount two (2) Form C contacts for remote switch position indication of the fault interrupter

- Junction box for wiring SF6 alarms, remote switch position contacts, or external power source for Electronic Control (specify NEMA 4X for dry applications or NEMA6P for wet/damp applications)

- Operation counters

- Refill kit consisting of regulator, hose and SF6 bottle

2.10 LABELING

A.	Hazard Alerting Signs

The exterior of the pad mount enclosure (if furnished) shall be provided with “Warning--Keep Out--Hazardous Voltage Inside--Can Shock, Burn, or Cause Death” signs.  Each unit of switchgear shall be provided with a “Danger--Hazardous Voltage--Failure to Follow These Instructions Will Likely Cause Shock, Burns, or Death” sign. The text shall further indicate that operating personnel must know and obey the employer’s work rules, know the hazards involved, and use proper protective equipment and tools to work on this equipment.  Each unit of switchgear shall be provided with a “Danger--Keep Away--Hazardous Voltage--Will Shock, Burn, or Cause Death” sign.

B.	Nameplates, Ratings Labels, and Connection Diagrams

Each unit of switchgear shall be provided with a nameplate indicating the manufacturer’s name, catalog number, model number, date of manufacture, and serial number.  Each unit of switchgear shall be provided with a ratings label indicating the following:  voltage rating; main bus continuous rating; short-circuit rating; fault interrupter ratings including interrupting and duty-cycle fault-closing; and load break switch ratings including duty-cycle fault-closing and short-time.